## Formatted
Table X - Microgrid Component Cost Comparisons
Case | A |  | B |  | C |  | D |  | E |  | F |  | G |  | H |  | I
Overview
Edelivered (GWh/yr) |  | 4.5684 |  | 4.5684 |  | 4.5684 |  | 4.5684 |  | - |  | - |  | - |  | - |  | - |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered |  | E_delivered
Ppeak (kW) |  | 84.9697 |  | 84.9697 |  | 84.9697 |  | 84.9697 |  | - |  | - |  | - |  | - |  | - |  | P_peak |  | P_peak |  | P_peak |  | P_peak |  | P_peak |  | P_peak |  | P_peak |  | P_peak |  | P_peak
CAPEX ($106) |  | 16.9063 |  | 140.2734 |  | 124.8485 |  | 98.1403 |  | - |  | - |  | - |  | - |  | - |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX |  | CAPEX
LCOE ($/MWh) |  | 187.4374 |  | 2009.2605 |  | 2376.6999 |  | 1848.3184 |  | - |  | - |  | - |  | - |  | - |  | LCOE |  | LCOE |  | LCOE |  | LCOE |  | LCOE |  | LCOE |  | LCOE |  | LCOE |  | LCOE
Tidal ((%)) ($/MWh) | 43.5322 | 81.5956 | 4.061 | 81.5958 | 3.1969 | 75.9809 | 4.1048 | 75.8688 | - | - | - | - | - | - | - | - | - | - | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost | LCOE_tidal_pct | LCOE_tidal_cost
Solar ((%)) ($/MWh) | 5.4913 | 10.2927 | 0.51226 | 10.2926 | 0.60017 | 14.2642 | 0.77542 | 14.3322 | - | - | - | - | - | - | - | - | - | - | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost | LCOE_solar_pct | LCOE_solar_cost
Grid ((%)) ($/MWh) | 2.1866e-07 | 4.0985e-07 | 2.0344e-08 | 4.0877e-07 | 1.9318e-08 | 4.5912e-07 | 2.396e-08 | 4.4286e-07 | - | - | - | - | - | - | - | - | - | - | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost | LCOE_grid_pct | LCOE_grid_cost
LIB ((%)) ($/MWh) | 6.0765 | 11.3896 | 1.4303 | 28.7383 | 75.0546 | 1783.8226 | 74.0072 | 1367.8888 | - | - | - | - | - | - | - | - | - | - | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost | LCOE_LIB_pct | LCOE_LIB_cost
Flow ((%)) ($/MWh) | 44.9 | 84.1595 | 93.9965 | 1888.6338 | 21.1483 | 502.6321 | 21.1126 | 390.2285 | - | - | - | - | - | - | - | - | - | - | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost | LCOE_flow_pct | LCOE_flow_cost
Batteries
Controller (hr) | [19 empty] | controller |  | controller |  | controller |  | controller |  | controller |  | controller |  | controller |  | controller |  | controller
Battery type | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow | LIB | Flow
Cost Total ($106) | 0.34794 | 7.6904 | 1.9696 | 129.4359 | 81.5018 | 34.4475 | 62.4981 | 26.744 | - | - | - | - | - | - | - | - | - | - | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow | bat_cost_total_LIB | bat_cost_total_flow
Cost Ecapacity ($106) | 0.34794 | 6.7619 | 1.5339 | 129.1518 | 80.8695 | 34.2136 | 61.9992 | 26.5854 | - | - | - | - | - | - | - | - | - | - | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow | bat_cost_E_LIB | bat_cost_E_flow
Cost Prated ($106) | - | 0.92853 | 0.43569 | 0.28413 | 0.63233 | 0.23381 | 0.49885 | 0.15853 | - | - | - | - | - | - | - | - | - | - | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow | bat_cost_P_LIB | bat_cost_P_flow
Ecapacity (MWh) | 1.5816 | 30 | 1.5816 | 573 | 217.3911 | 745 | 217.5411 | 573 | - | - | - | - | - | - | - | - | - | - | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow | bat_cap_E_LIB | bat_cost_cap_flow
Prated (MW) | 0.77138 | 0.92853 | 0.77138 | 0.92853 | 1.6297 | 0.51958 | 1.6302 | 0.51808 | - | - | - | - | - | - | - | - | - | - | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow | bat_rated_P_LIB | bat_rated_P_flow
Cost/Ecapacity ($/kWh) | 220 | 30 | 969.84 | 573 | 372 | 745 | 285 | 573 | - | - | - | - | - | - | - | - | - | - | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow | bat_cost_cap_LIB | bat_cost_cap_flow
Cost/Prated ($/kW) | - | 1000 | 564.82 | 306 | 388 | 450 | 306 | 306 | - | - | - | - | - | - | - | - | - | - | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow | bat_cost_rated_LIB | bat_cost_rated_flow
Life (cycles) |  | - |  | - |  | - |  | 10000 |  | - |  | - |  | - |  | - |  | - |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow |  | bat_max_cycles_flow
Life (years) | 6.6863 | 20 | 15 | 15 | 10 | 15 | 10 | 15 | - | - | - | - | - | - | - | - | - | - | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow | bat_life_LIB | bat_life_flow
E/P ratio (hours) | 2.0503 | 242.7452 | 2.0503 | 242.7456 | 133.3913 | 88.387 | 133.4426 | 89.5557 | - | - | - | - | - | - | - | - | - | - | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow | bat_E_P_LIB | bat_E_P_flow
Generators | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal | Solar | Tidal
Cost Total ($106) | 1.411 | 7.457 | 1.411 | 7.457 | 1.9554 | 6.9438 | 1.9647 | 6.9336 | - | - | - | - | - | - | - | - | - | - | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal | gen_cost_total_solar | gen_cost_total_tidal
Prated (MW) | 0.50392 | 1.7342 | 0.50391 | 1.7342 | 0.69836 | 1.6148 | 0.70168 | 1.6125 | - | - | - | - | - | - | - | - | - | - | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal | gen_rated_power_solar | gen_rated_power_tidal
Cost/Prated ($/W) | 2.8 | 4.3 | 2.8 | 4.3 | 2.8 | 4.3 | 2.8 | 4.3 | - | - | - | - | - | - | - | - | - | - | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal | gen_power_cost_solar | gen_power_cost_tidal
Life (years) | 30 | 20 | 30 | 20 | 30 | 20 | 30 | 20 | - | - | - | - | - | - | - | - | - | - | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal | gen_life_solar | gen_life_tidal
Capacity factor (%) | 16.6193 | 25.2442 | 16.6193 | 25.2442 | 16.6193 | 25.2442 | 16.6193 | 25.2442 | - | - | - | - | - | - | - | - | - | - | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal | gen_CF_solar | gen_CF_tidal
| A - Partical Swarm - make_island_aspirational | [5 empty] | D - Partical Swarm - make_island_PNNL2019_2025 | [5 empty] | G - -
| B - Partical Swarm - make_island_Zakeri2015 | [5 empty] | E - - | [5 empty] | H - -
| C - Partical Swarm - make_island_PNNL2019_2018 | [5 empty] | F - - | [5 empty] | J - -
| 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 6 | 6 | 7 | 7 | 8 | 8 | 9 | 9

## data
'title' | 'Partical Swarm - make_island_aspirational' | 'Partical Swarm - make_island_Zakeri2015' | 'Partical Swarm - make_island_PNNL2019_2018' | 'Partical Swarm - make_island_PNNL2019_2025'
'E_delivered' | 4.5684 | 4.5684 | 4.5684 | 4.5684
'P_peak' | 84.9697 | 84.9697 | 84.9697 | 84.9697
'CAPEX' | 16.9063 | 140.2734 | 124.8485 | 98.1403
'LCOE' | 187.4374 | 2009.2605 | 2376.6999 | 1848.3184
'LCOE_tidal_cost' | 81.5956 | 81.5958 | 75.9809 | 75.8688
'LCOE_tidal_pct' | 43.5322 | 4.061 | 3.1969 | 4.1048
'LCOE_solar_cost' | 10.2927 | 10.2926 | 14.2642 | 14.3322
'LCOE_solar_pct' | 5.4913 | 0.51226 | 0.60017 | 0.77542
'LCOE_grid_cost' | 4.0985e-07 | 4.0877e-07 | 4.5912e-07 | 4.4286e-07
'LCOE_grid_pct' | 2.1866e-07 | 2.0344e-08 | 1.9318e-08 | 2.396e-08
'LCOE_LIB_cost' | 11.3896 | 28.7383 | 1783.8226 | 1367.8888
'LCOE_LIB_pct' | 6.0765 | 1.4303 | 75.0546 | 74.0072
'LCOE_flow_cost' | 84.1595 | 1888.6338 | 502.6321 | 390.2285
'LCOE_flow_pct' | 44.9 | 93.9965 | 21.1483 | 21.1126
'controller' | 6.3195 | 5.1076 | 8504.4311 | 34286.2595
'bat_cost_total_LIB' | 0.34794 | 1.9696 | 81.5018 | 62.4981
'bat_cost_total_flow' | 7.6904 | 129.4359 | 34.4475 | 26.744
'bat_cost_E_LIB' | 0.34794 | 1.5339 | 80.8695 | 61.9992
'bat_cost_E_flow' | 6.7619 | 129.1518 | 34.2136 | 26.5854
'bat_cost_P_LIB' | 0 | 0.43569 | 0.63233 | 0.49885
'bat_cost_P_flow' | 0.92853 | 0.28413 | 0.23381 | 0.15853
'bat_cap_E_LIB' | 1.5816 | 1.5816 | 217.3911 | 217.5411
'bat_cap_E_flow' | 225.3956 | 225.3957 | 45.9244 | 46.3969
'bat_rated_P_LIB' | 0.77138 | 0.77138 | 1.6297 | 1.6302
'bat_rated_P_flow' | 0.92853 | 0.92853 | 0.51958 | 0.51808
'bat_cost_cap_LIB' | 220 | 969.84 | 372 | 285
'bat_cost_cap_flow' | 30 | 573 | 745 | 573
'bat_cost_rated_LIB' | 0 | 564.82 | 388 | 306
'bat_cost_rated_flow' | 1000 | 306 | 450 | 306
'bat_max_cycles_LIB' | [] | [] | [] | 3500
'bat_max_cycles_flow' | [] | [] | [] | 10000
'bat_life_LIB' | 6.6863 | 15 | 10 | 10
'bat_life_flow' | 20 | 15 | 15 | 15
'bat_E_P_LIB' | 2.0503 | 2.0503 | 133.3913 | 133.4426
'bat_E_P_flow' | 242.7452 | 242.7456 | 88.387 | 89.5557
'gen_cost_total_solar' | 1.411 | 1.411 | 1.9554 | 1.9647
'gen_cost_total_tidal' | 7.457 | 7.457 | 6.9438 | 6.9336
'gen_rated_power_solar' | 0.50392 | 0.50391 | 0.69836 | 0.70168
'gen_rated_power_tidal' | 1.7342 | 1.7342 | 1.6148 | 1.6125
'gen_power_cost_solar' | 2.8 | 2.8 | 2.8 | 2.8
'gen_power_cost_tidal' | 4.3 | 4.3 | 4.3 | 4.3
'gen_life_solar' | 30 | 30 | 30 | 30
'gen_life_tidal' | 20 | 20 | 20 | 20
'gen_CF_solar' | 16.6193 | 16.6193 | 16.6193 | 16.6193
'gen_CF_tidal' | 25.2442 | 25.2442 | 25.2442 | 25.2442

## preprocessed
title | Partical Swarm - make_island_aspirational | Partical Swarm - make_island_Zakeri2015 | Partical Swarm - make_island_PNNL2019_2018 | Partical Swarm - make_island_PNNL2019_2025 | - | - | - | - | - | -
E_delivered | 4.5684 | 4.5684 | 4.5684 | 4.5684 | - | - | - | - | - | -
P_peak | 84.9697 | 84.9697 | 84.9697 | 84.9697 | - | - | - | - | - | -
CAPEX | 16.9063 | 140.2734 | 124.8485 | 98.1403 | - | - | - | - | - | -
LCOE | 187.4374 | 2009.2605 | 2376.6999 | 1848.3184 | - | - | - | - | - | -
LCOE_tidal_cost | 81.5956 | 81.5958 | 75.9809 | 75.8688 | - | - | - | - | - | -
LCOE_tidal_pct | 43.5322 | 4.061 | 3.1969 | 4.1048 | - | - | - | - | - | -
LCOE_solar_cost | 10.2927 | 10.2926 | 14.2642 | 14.3322 | - | - | - | - | - | -
LCOE_solar_pct | 5.4913 | 0.51226 | 0.60017 | 0.77542 | - | - | - | - | - | -
LCOE_grid_cost | 4.0985e-07 | 4.0877e-07 | 4.5912e-07 | 4.4286e-07 | - | - | - | - | - | -
LCOE_grid_pct | 2.1866e-07 | 2.0344e-08 | 1.9318e-08 | 2.396e-08 | - | - | - | - | - | -
LCOE_LIB_cost | 11.3896 | 28.7383 | 1783.8226 | 1367.8888 | - | - | - | - | - | -
LCOE_LIB_pct | 6.0765 | 1.4303 | 75.0546 | 74.0072 | - | - | - | - | - | -
LCOE_flow_cost | 84.1595 | 1888.6338 | 502.6321 | 390.2285 | - | - | - | - | - | -
LCOE_flow_pct | 44.9 | 93.9965 | 21.1483 | 21.1126 | - | - | - | - | - | -
controller | 6.3195 | 5.1076 | 8504.4311 | 34286.2595 | - | - | - | - | - | -
bat_cost_total_LIB | 0.34794 | 1.9696 | 81.5018 | 62.4981 | - | - | - | - | - | -
bat_cost_total_flow | 7.6904 | 129.4359 | 34.4475 | 26.744 | - | - | - | - | - | -
bat_cost_E_LIB | 0.34794 | 1.5339 | 80.8695 | 61.9992 | - | - | - | - | - | -
bat_cost_E_flow | 6.7619 | 129.1518 | 34.2136 | 26.5854 | - | - | - | - | - | -
bat_cost_P_LIB | - | 0.43569 | 0.63233 | 0.49885 | - | - | - | - | - | -
bat_cost_P_flow | 0.92853 | 0.28413 | 0.23381 | 0.15853 | - | - | - | - | - | -
bat_cap_E_LIB | 1.5816 | 1.5816 | 217.3911 | 217.5411 | - | - | - | - | - | -
bat_cap_E_flow | 225.3956 | 225.3957 | 45.9244 | 46.3969 | - | - | - | - | - | -
bat_rated_P_LIB | 0.77138 | 0.77138 | 1.6297 | 1.6302 | - | - | - | - | - | -
bat_rated_P_flow | 0.92853 | 0.92853 | 0.51958 | 0.51808 | - | - | - | - | - | -
bat_cost_cap_LIB | 220 | 969.84 | 372 | 285 | - | - | - | - | - | -
bat_cost_cap_flow | 30 | 573 | 745 | 573 | - | - | - | - | - | -
bat_cost_rated_LIB | - | 564.82 | 388 | 306 | - | - | - | - | - | -
bat_cost_rated_flow | 1000 | 306 | 450 | 306 | - | - | - | - | - | -
bat_max_cycles_LIB | - | - | - | 3500 | - | - | - | - | - | -
bat_max_cycles_flow | - | - | - | 10000 | - | - | - | - | - | -
bat_life_LIB | 6.6863 | 15 | 10 | 10 | - | - | - | - | - | -
bat_life_flow | 20 | 15 | 15 | 15 | - | - | - | - | - | -
bat_E_P_LIB | 2.0503 | 2.0503 | 133.3913 | 133.4426 | - | - | - | - | - | -
bat_E_P_flow | 242.7452 | 242.7456 | 88.387 | 89.5557 | - | - | - | - | - | -
gen_cost_total_solar | 1.411 | 1.411 | 1.9554 | 1.9647 | - | - | - | - | - | -
gen_cost_total_tidal | 7.457 | 7.457 | 6.9438 | 6.9336 | - | - | - | - | - | -
gen_rated_power_solar | 0.50392 | 0.50391 | 0.69836 | 0.70168 | - | - | - | - | - | -
gen_rated_power_tidal | 1.7342 | 1.7342 | 1.6148 | 1.6125 | - | - | - | - | - | -
gen_power_cost_solar | 2.8 | 2.8 | 2.8 | 2.8 | - | - | - | - | - | -
gen_power_cost_tidal | 4.3 | 4.3 | 4.3 | 4.3 | - | - | - | - | - | -
gen_life_solar | 30 | 30 | 30 | 30 | - | - | - | - | - | -
gen_life_tidal | 20 | 20 | 20 | 20 | - | - | - | - | - | -
gen_CF_solar | 16.6193 | 16.6193 | 16.6193 | 16.6193 | - | - | - | - | - | -
gen_CF_tidal | 25.2442 | 25.2442 | 25.2442 | 25.2442 | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | -